## Sheet1 (hidden)
|  | Preventive Maintainance | [6 empty] | Proactive Maintainance | [6 empty] | Corrective Maintainance
SN | Asset Name | Daily | Weekly | Fortnightly | Monthly | Quarterly | Half yearly | Yearly | Daily | Weekly | Fortnightly | Monthly | Quarterly | Half yearly | Yearly | Daily | Weekly | Fortnightly | Monthly | Quarterly | Half yearly | Yearly
1 | ACDB |  |  |  | Monthly Inhouse PM | Inhouse Thermography
2 | ACS |  |  |  | Monthly Inhouse PM | Quarterly PM- AMC
3 | Air Conditioner |  |  |  | Monthly Inhouse PM | Quarterly PM- AMC |  |  | Hourly Readings |  |  | Infra alarm Testing
4 | Air Purifier |  |  |  | Monthly Inhouse PM | Quarterly PM- AMC
5 | BMS |  |  |  | Monthly Inhouse PM | Quarterly PM- AMC
6 | CCTV |  |  |  | Monthly Inhouse PM | Quarterly PM- AMC
7 | Comfort AC |  |  |  | Monthly Inhouse PM | Quarterly PM- AMC
8 | DCDB |  |  |  | Monthly Inhouse PM | Inhouse Thermography
9 | DG Battery |  |  |  | Monthly Inhouse PM | -
10 | Diesel Generator |  |  |  | Monthly Inhouse PM | Quarterly PM- AMC |  | B/C Check | Daily A Check | On load Testing* |  | Infra alarm Testing
11 | Earth Pit |  |  |  | Monthly Inhouse PM | Quarterly PM- AMC
12 | Fire and Safety |  |  |  | Monthly Inhouse PM | Quarterly PM- AMC | [6 empty] | Infra alarm Testing
13 | FM-200 |  |  |  | Monthly Inhouse PM | Quarterly PM- AMC | [6 empty] | Infra alarm Testing
14 | HT Panel |  |  |  | Monthly Inhouse PM | Quarterly PM- AMC |  | Annual OEM PM & Breaker servicing |  |  |  | Infra alarm Testing
15 | Inverter |  |  |  | Monthly Inhouse PM | -
16 | Isolation Transformer |  |  |  | Monthly Inhouse PM | -
17 | LT Panel |  |  |  | Monthly Inhouse PM | Quarterly PM- AMC |  | ACB Annual Servicing |  |  |  | Infra alarm Testing
18 | PAS |  |  |  | Monthly Inhouse PM | Quarterly PM- AMC
19 | PFE |  |  |  | Monthly Inhouse PM | -
20 | RRS |  |  |  | Monthly Inhouse PM | Quarterly PM- AMC
21 | Servo Stabilizer |  |  |  | Monthly Inhouse PM | Quarterly PM- AMC
22 | Smoke Detector |  |  |  | Monthly Inhouse PM | Quarterly PM- AMC | [6 empty] | Infra alarm Testing
| SMPS- Vertiv |  |  |  | Monthly Inhouse PM | - | OEM PM | - | Hourly Readings |  |  | Infra alarm Testing
23 | SMPS- Delta |  |  |  | Monthly Inhouse PM | - | - | OEM PM | Hourly Readings |  |  | Infra alarm Testing
24 | SMPS BB |  |  |  | Monthly Inhouse PM- IR Test | Online Discharge test |  | Deep Discharge Test
25 | Solar System |  |  |  | Monthly Inhouse PM | - |  |  |  | Dry/Wet Cleaning
26 | Transformer |  |  |  | Monthly Inhouse PM | Quarterly PM- AMC |  | Annual PM(Oil filteration & Dehydration)
27 | UPS |  |  |  | Monthly Inhouse PM | Quarterly PM- AMC |  |  | Hourly Readings |  |  | Infra alarm Testing
28 | UPS BB |  |  |  | Monthly Inhouse PM- IR Test | Online Discharge test
29 | VESDA |  |  |  | Monthly Inhouse PM | Quarterly PM- AMC | [6 empty] | Infra alarm Testing
30 | WLD |  |  |  | Monthly Inhouse PM | Quarterly PM- AMC | [6 empty] | Infra alarm Testing

## Sheet3
MOP Approval Required (Y/N) | Y | Activity type | Count | CRQ required
|  | Corrective Maintainance | 31 | 5
Row Labels | Count of Activity Category | Preventive Maintainance | 62 | 28
Corrective Maintainance | 14 | Proactive Maintainance | 54 | 32
Preventive Maintainance | 62 | Total | 147 | 65
Proactive Maintainance | 44
Grand Total | 120

## Activity List
SN | Asset Name | Frequency | Activity Category | Activity Name | CRQ Required (Y/N) | PTW Required (Y/N) | MOP Approval Required (Y/N) | Activity performed by OEM/O&M | Challenges | Day/Night time as per O&M | Alarms generated | Max. Alarms time | Pre -Photo required | Post photo required
1 | ACDB | Monthly | Preventive Maintenance | Monthly Inhouse PM | N | Y | Y | O&M |  | Day | No | NA | Yes | Yes
2 | ACDB | Quarterly | Preventive Maintenance | Inhouse Thermography | N | Y | Y | O&M |  | Day | No | NA | Yes | Yes
3 | ACS | Monthly | Preventive Maintenance | Monthly Inhouse PM | N | Y | Y | O&M |  | Day | No | NA | Yes | Yes
4 | ACS | Quarterly | Preventive Maintenance | Quarterly PM- AMC | N | Y | Y | OEM |  | Day | No | NA | Yes | Yes
5 | Air Conditioner | Daily | Preventive Maintenance | Dry/Wet Cleaning | N | Y | N | O&M |  | SOS | No | NA | Yes | Yes
6 | Air Conditioner | Daily | Not Required as no activity involved | Hourly Readings | N | Y | N | O&M |  | Day/Night | No | NA | No | No
7 | Air Conditioner | Monthly | Preventive Maintenance | Monthly Inhouse PM | Y | Y | Y | O&M |  | Day | Yes | 15 Min | Yes | Yes
8 | Air Conditioner | Quarterly | Preventive Maintenance | Quarterly PM- AMC | Y | Y | Y | OEM | PM Continues for 7-8 Days | Day | Yes | 60 Min | Yes | Yes
9 | Air Conditioner | Monthly | Proactive Maintenance | Infra alarm Testing | Y | Y | Y | O&M |  | Day | Yes | 15 Min | No | No
10 | Air Purifier | Monthly | Preventive Maintenance | Monthly Inhouse PM | N | Y | Y | O&M |  | Day | No | NA | Yes | Yes
11 | Air Purifier | Quarterly | Preventive Maintenance | Quarterly PM- AMC | N | Y | Y | OEM |  | Day | No | NA | Yes | Yes
12 | BMS | Monthly | Preventive Maintenance | Monthly Inhouse PM | Y | Y | Y | O&M |  | Day | Yes | 15 Min | Yes | Yes
13 | BMS | Quarterly | Preventive Maintenance | Quarterly PM- AMC | Y | Y | Y | OEM | PM Continues for 7-8 Days | Day | Yes | 60 Min | Yes | Yes
14 | CCTV | Monthly | Preventive Maintenance | Monthly Inhouse PM | N | Y | Y | O&M |  | Day | No | NA | Yes | Yes
15 | CCTV | Quarterly | Preventive Maintenance | Quarterly PM- AMC | N | Y | Y | OEM | PM Continues for 7-8 Days | Day | No | NA | Yes | Yes
16 | Comfort AC | Monthly | Preventive Maintenance | Monthly Inhouse PM | N | Y | Y | O&M |  | Day | No | NA | Yes | Yes
17 | Comfort AC | Quarterly | Preventive Maintenance | Quarterly PM- AMC | N | Y | Y | OEM |  | Day | No | NA | Yes | Yes
18 | DCDB | Monthly | Preventive Maintenance | Monthly Inhouse PM | N | Y | Y | O&M |  | Day | No | NA | Yes | Yes
19 | DCDB | Quarterly | Preventive Maintenance | Inhouse Thermography | N | Y | Y | O&M |  | Day | No | NA | Yes | Yes
20 | DG Battery | Monthly | Preventive Maintenance | Monthly Inhouse PM | N | Y | Y | O&M |  | Day | No | NA | Yes | Yes
21 | Diesel Generator | Daily | Proactive Maintenance | Daily A Check | Y | Y | N | O&M |  | Day | Yes | 15 Min | Yes | Yes
22 | Diesel Generator | Daily | Proactive Maintenance | Diesel Refilling | N | Y | N | O&M |  | SOS | No | NA | Yes | Yes
23 | Diesel Generator | Weekly | Proactive Maintenance | On load Testing* | Y | Y | N | O&M |  | Day | Yes | 15 Min | Yes | Yes
24 | Diesel Generator | Monthly | Preventive Maintenance | Monthly Inhouse PM | Y | Y | Y | O&M |  | Day | Yes | 15 Min | Yes | Yes
25 | Diesel Generator | Quarterly | Preventive Maintenance | Quarterly PM- AMC | Y | Y | Y | OEM |  | Day | Yes | 60 Min | Yes | Yes
26 | Diesel Generator | Yearly | Preventive Maintenance | B/C Check | Y | Y | Y | OEM |  | Day | Yes | 6 Hrs | Yes | Yes
27 | Diesel Generator | Monthly | Proactive Maintenance | Infra alarm Testing | Y | Y | Y | O&M |  | Day | Yes | 15 Min | No | No
28 | Earth Pit | Monthly | Preventive Maintenance | Monthly Inhouse PM | N | Y | Y | O&M |  | Day | No | NA | Yes | Yes
29 | Earth Pit | Quarterly | Preventive Maintenance | Quarterly PM- AMC | N | Y | Y | OEM |  | Day | No | NA | Yes | Yes
30 | Fire and Safety | Monthly | Preventive Maintenance | Monthly Inhouse PM | Y | Y | Y | O&M |  | Day | Yes | 15 Min | Yes | Yes
31 | Fire and Safety | Quarterly | Preventive Maintenance | Quarterly PM- AMC | Y | Y | Y | OEM | PM Continues for 7-8 Days | Day | Yes | 15 Min | Yes | Yes
32 | Fire and Safety | Quarterly | Proactive Maintenance | Infra alarm Testing | Y | Y | Y | OEM |  | Day | Yes | 15 Min | No | No
33 | FM-200 | Monthly | Preventive Maintenance | Monthly Inhouse PM | Y | Y | Y | O&M |  | Day | Yes | 15 Min | Yes | Yes
34 | FM-200 | Quarterly | Preventive Maintenance | Quarterly PM- AMC | Y | Y | Y | OEM | PM Continues for 7-8 Days | Day | Yes | 15 Min | Yes | Yes
35 | FM-200 | Quarterly | Proactive Maintenance | Infra alarm Testing | Y | Y | Y | OEM |  | Day | Yes | 15 Min | No | No
36 | HT Panel | Monthly | Preventive Maintenance | Monthly Inhouse PM | Y | Y | Y | O&M |  | Day | Yes | 15 Min | Yes | Yes
37 | HT Panel | Quarterly | Preventive Maintenance | Quarterly PM- AMC | Y | Y | Y | OEM |  | Day | Yes | 60 Min | Yes | Yes
38 | HT Panel | Yearly | Preventive Maintenance | Annual OEM PM & Breaker servicing | Y | Y | Y | OEM |  | Day | Yes | 60 Min | Yes | Yes
39 | HT Panel | Monthly | Proactive Maintenance | Infra alarm Testing | Y | Y | Y | O&M |  | Day | Yes | 15 Min | No | No
40 | Inverter | Monthly | Preventive Maintenance | Monthly Inhouse PM | N | Y | Y | O&M |  | Day | No | NA | Yes | Yes
41 | Isolation Transformer | Monthly | Preventive Maintenance | Monthly Inhouse PM | N | Y | Y | O&M |  | Day | No | NA | Yes | Yes
42 | LT Panel | Monthly | Preventive Maintenance | Monthly Inhouse PM | Y | Y | Y | O&M |  | Day | Yes | 15 Min | Yes | Yes
43 | LT Panel | Quarterly | Preventive Maintenance | Quarterly PM- AMC | Y | Y | Y | OEM |  | Day | Yes | 60 Min | Yes | Yes
44 | LT Panel | Yearly | Preventive Maintenance | ACB Annual Servicing | Y | Y | Y | OEM |  | Day | Yes | 60 Min | Yes | Yes
45 | LT Panel | Monthly | Proactive Maintenance | Infra alarm Testing | Y | Y | Y | O&M |  | Day | Yes | 15 Min | No | No
46 | PAS | Monthly | Preventive Maintenance | Monthly Inhouse PM | N | Y | Y | O&M |  | Day | No | NA | Yes | Yes
47 | PAS | Quarterly | Preventive Maintenance | Quarterly PM- AMC | N | Y | Y | OEM |  | Day | No | NA | Yes | Yes
48 | PFE | Monthly | Preventive Maintenance | Monthly Inhouse PM | N | Y | Y | O&M |  | Day | No | NA | Yes | Yes
49 | RRS | Monthly | Preventive Maintenance | Monthly Inhouse PM | N | Y | Y | O&M |  | Day | No | NA | Yes | Yes
50 | RRS | Quarterly | Preventive Maintenance | Quarterly PM- AMC | N | Y | Y | OEM | PM Continues for 7-8 Days | Day | No | NA | Yes | Yes
51 | Servo Stabilizer | Monthly | Preventive Maintenance | Monthly Inhouse PM | N | Y | Y | O&M |  | Day | No | NA | Yes | Yes
52 | Servo Stabilizer | Quarterly | Preventive Maintenance | Quarterly PM- AMC | N | Y | Y | OEM |  | Day | No | NA | Yes | Yes
53 | Smoke Detector | Monthly | Preventive Maintenance | Monthly Inhouse PM | N | Y | Y | O&M |  | Day | Yes | 15 Min | Yes | Yes
54 | Smoke Detector | Quarterly | Preventive Maintenance | Quarterly PM- AMC | Y | Y | Y | OEM |  | Day | Yes | 15 Min | Yes | Yes
55 | Smoke Detector | Quarterly | Proactive Maintenance | Infra alarm Testing | Y | Y | Y | OEM |  | Day | Yes | 15 Min | No | No
56 | SMPS- Vertiv | Daily | Not Required as no activity involved | Hourly Readings | N | Y | N | O&M |  | Day/Night | No | NA | No | No
57 | SMPS- Vertiv | Monthly | Preventive Maintenance | Monthly Inhouse PM | N | Y | Y | O&M |  | Day | Yes | 15 Min | Yes | Yes
58 | SMPS- Vertiv | Half yearly | Preventive Maintenance | OEM PM | Y | Y | Y | OEM |  | Night | Yes | 6 Hrs | Yes | Yes
59 | SMPS- Vertiv | Monthly | Proactive Maintenance | Infra alarm Testing | N | Y | Y | O&M |  | Night | Yes | 15 Min | No | No
60 | SMPS- Delta | Daily | Not Required as no activity involved | Hourly Readings | N | Y | N | O&M |  | Day/Night | No | NA | No | No
61 | SMPS- Delta | Monthly | Preventive Maintenance | Monthly Inhouse PM | N | Y | Y | O&M |  | Day | Yes | 15 Min | Yes | Yes
62 | SMPS- Delta | Yearly | Preventive Maintenance | OEM PM | Y | Y | Y | OEM |  | Night | Yes | 6 Hrs | Yes | Yes
63 | SMPS- Delta | Monthly | Proactive Maintenance | Infra alarm Testing | N | Y | Y | O&M |  | Night | Yes | 15 Min | No | No
64 | SMPS BB | Monthly | Preventive Maintenance | Monthly Inhouse PM- IR Test | N | Y | Y | O&M |  | Day | No | NA | Yes | Yes
65 | SMPS BB | Quarterly | Preventive Maintenance | Online Discharge test | Y | Y | Y | O&M |  | Night | No | NA | Yes | Yes
66 | SMPS BB | Yearly | Preventive Maintenance | Deep Discharge Test | Y | Y | Y | O&M |  | Night | No | NA | Yes | Yes
67 | Solar System | Weekly | Preventive Maintenance | Dry/Wet Cleaning | N | Y | N | O&M |  | Day | No | NA | Yes | Yes
68 | Solar System | Monthly | Preventive Maintenance | Monthly Inhouse PM | N | Y | Y | O&M |  | Day | No | NA | Yes | Yes
69 | Transformer | Monthly | Preventive Maintenance | Monthly Inhouse PM | N | Y | Y | O&M |  | Day | Yes | 15 Min | Yes | Yes
70 | Transformer | Quarterly | Preventive Maintenance | Quarterly PM- AMC | Y | Y | Y | OEM |  | Day | Yes | 60 Min | Yes | Yes
71 | Transformer | Yearly | Preventive Maintenance | Annual PM(Oil filteration & Dehydration) | N | Y | Y | OEM |  | Day | Yes | 6 Hrs | Yes | Yes
72 | UPS | Daily | Not Required as no activity involved | Hourly Readings | N | Y | N | O&M |  | Day/Night | No | NA | No | No
73 | UPS | Monthly | Preventive Maintenance | Monthly Inhouse PM | Y | Y | Y | O&M |  | Day | Yes | 15 Min | Yes | Yes
74 | UPS | Quarterly | Preventive Maintenance | Quarterly PM- AMC | Y | Y | Y | OEM |  | Night | Yes | 6 Hrs | Yes | Yes
75 | UPS | Monthly | Proactive Maintenance | Infra alarm Testing | Y | Y | Y | O&M |  | Night | Yes | 15 Min | No | No
76 | UPS BB | Monthly | Preventive Maintenance | Monthly Inhouse PM- IR Test | N | Y | Y | O&M |  | Day | No | NA | Yes | Yes
77 | UPS BB | Quarterly | Preventive Maintenance | Online Discharge test | Y | Y | Y | O&M |  | Night | No | NA | Yes | Yes
78 | VESDA | Monthly | Preventive Maintenance | Monthly Inhouse PM | N | Y | Y | O&M |  | Day | Yes | 15 Min | Yes | Yes
79 | VESDA | Quarterly | Preventive Maintenance | Quarterly PM- AMC | Y | Y | Y | OEM | PM Continues for 7-8 Days | Day | Yes | 15 Min | Yes | Yes
80 | VESDA | Quarterly | Proactive Maintenance | Infra alarm Testing | Y | Y | Y | OEM |  | Day | Yes | 15 Min | No | No
81 | WLD | Monthly | Preventive Maintenance | Monthly Inhouse PM | N | Y | Y | O&M |  | Day | Yes | 15 Min | Yes | Yes
82 | WLD | Quarterly | Preventive Maintenance | Quarterly PM- AMC | Y | Y | Y | OEM | PM Continues for 7-8 Days | Day | Yes | 15 Min | Yes | Yes
83 | WLD | Quarterly | Proactive Maintenance | Infra alarm Testing | Y | Y | Y | OEM |  | Day | Yes | 15 Min | No | No
84 | ACDB | - | Corrective Maintenance | All Corrective Maintainance | N | Y | Y | O&M |  | SOS | No | NA | Yes | Yes
85 | ACS | - | Corrective Maintenance | All Corrective Maintainance | N | Y | N | OEM |  | SOS | No | NA | Yes | Yes
86 | Air Conditioner | - | Corrective Maintenance | All Corrective Maintainance | N | Y | Y | OEM |  | SOS | Yes | To be discussed | Yes | Yes
87 | Air Purifier | - | Corrective Maintenance | All Corrective Maintainance | N | Y | N | OEM |  | SOS | No | NA | Yes | Yes
88 | BMS | - | Corrective Maintenance | All Corrective Maintainance | Y | Y | N | OEM |  | SOS | Yes | To be discussed | Yes | Yes
89 | CCTV | - | Corrective Maintenance | All Corrective Maintainance | N | Y | N | OEM |  | SOS | No | NA | Yes | Yes
90 | Comfort AC | - | Corrective Maintenance | All Corrective Maintainance | N | Y | N | OEM |  | SOS | No | NA | Yes | Yes
91 | DCDB | - | Corrective Maintenance | All Corrective Maintainance | N | Y | Y | O&M |  | SOS | No | NA | Yes | Yes
92 | DG Battery | - | Corrective Maintenance | All Corrective Maintainance | N | Y | N | O&M |  | SOS | No | NA | Yes | Yes
93 | Diesel Generator | - | Corrective Maintenance | All Corrective Maintainance | N | Y | Y | OEM |  | SOS | Yes | To be discussed | Yes | Yes
94 | Earth Pit | - | Corrective Maintenance | All Corrective Maintainance | N | Y | N | O&M |  | SOS | No | NA | Yes | Yes
95 | Fire and Safety | - | Corrective Maintenance | All Corrective Maintainance | N | Y | N | OEM |  | SOS | Yes | To be discussed | Yes | Yes
96 | FM-200 | - | Corrective Maintenance | All Corrective Maintainance | N | Y | N | OEM |  | SOS | Yes | To be discussed | Yes | Yes
97 | HT Panel | - | Corrective Maintenance | All Corrective Maintainance | N | Y | Y | OEM |  | SOS | Yes | To be discussed | Yes | Yes
98 | Inverter | - | Corrective Maintenance | All Corrective Maintainance | N | Y | N | OEM |  | SOS | No | NA | Yes | Yes
99 | Isolation Transformer | - | Corrective Maintenance | All Corrective Maintainance | N | Y | Y | OEM |  | SOS | No | NA | Yes | Yes
100 | LT Panel | - | Corrective Maintenance | All Corrective Maintainance | N | Y | Y | OEM |  | SOS | Yes | To be discussed | Yes | Yes
101 | PAS | - | Corrective Maintenance | All Corrective Maintainance | N | Y | N | OEM |  | SOS | No | NA | Yes | Yes
102 | PFE | - | Corrective Maintenance | All Corrective Maintainance | N | Y | N | O&M |  | SOS | No | NA | Yes | Yes
103 | RRS | - | Corrective Maintenance | All Corrective Maintainance | N | Y | N | OEM |  | SOS | No | NA | Yes | Yes
104 | Servo Stabilizer | - | Corrective Maintenance | All Corrective Maintainance | N | Y | Y | OEM |  | SOS | No | NA | Yes | Yes
105 | Smoke Detector | - | Corrective Maintenance | All Corrective Maintainance | N | Y | N | OEM |  | SOS | Yes | To be discussed | Yes | Yes
106 | SMPS- Vertiv | - | Corrective Maintenance | All Corrective Maintainance | Y | Y | Y | OEM |  | SOS | Yes | To be discussed | Yes | Yes
107 | SMPS- Delta | - | Corrective Maintenance | All Corrective Maintainance | Y | Y | Y | OEM |  | SOS | Yes | To be discussed | Yes | Yes
108 | SMPS BB | - | Corrective Maintenance | All Corrective Maintainance | Y | Y | Y | OEM |  | SOS | No | NA | Yes | Yes
109 | Solar System | - | Corrective Maintenance | All Corrective Maintainance | N | Y | N | OEM |  | SOS | No | NA | Yes | Yes
110 | Transformer | - | Corrective Maintenance | All Corrective Maintainance | N | Y | Y | OEM |  | SOS | Yes | To be discussed | Yes | Yes
111 | UPS | - | Corrective Maintenance | All Corrective Maintainance | N | Y | Y | OEM |  | SOS | Yes | To be discussed | Yes | Yes
112 | UPS BB | - | Corrective Maintenance | All Corrective Maintainance | Y | Y | Y | OEM |  | SOS | No | NA | Yes | Yes
113 | VESDA | - | Corrective Maintenance | All Corrective Maintainance | N | Y | N | OEM |  | SOS | Yes | To be discussed | Yes | Yes
114 | WLD | - | Corrective Maintenance | All Corrective Maintainance | N | Y | N | OEM |  | SOS | Yes | To be discussed | Yes | Yes
115 | ACDB | EOL as per schedule | Proactive Maintenance | EOL Replacement | Y | Y | Y | OEM |  | Night | No | NA | Yes | Yes
116 | ACS | EOL as per schedule | Proactive Maintenance | EOL Replacement | N | Y | Y | OEM |  | Day | No | NA | Yes | Yes
117 | Air Conditioner | EOL as per schedule | Proactive Maintenance | EOL Replacement | Y | Y | Y | OEM |  | Day | Yes | To be discussed | Yes | Yes
118 | Air Purifier | EOL as per schedule | Proactive Maintenance | EOL Replacement | N | Y | Y | OEM |  | Day | No | NA | Yes | Yes
119 | BMS | EOL as per schedule | Proactive Maintenance | EOL Replacement | Y | Y | Y | OEM |  | Day | Yes | To be discussed | Yes | Yes
120 | CCTV | EOL as per schedule | Proactive Maintenance | EOL Replacement | N | Y | Y | OEM |  | Day | No | NA | Yes | Yes
121 | Comfort AC | EOL as per schedule | Proactive Maintenance | EOL Replacement | N | Y | Y | OEM |  | Day | No | NA | Yes | Yes
122 | DCDB | EOL as per schedule | Proactive Maintenance | EOL Replacement | Y | Y | Y | OEM |  | Night | No | NA | Yes | Yes
123 | DG Battery | EOL as per schedule | Proactive Maintenance | EOL Replacement | N | Y | Y | O&M |  | Day | No | NA | Yes | Yes
124 | Diesel Generator | EOL as per schedule | Proactive Maintenance | EOL Replacement | Y | Y | Y | OEM |  | Day | Yes | To be discussed | Yes | Yes
125 | Earth Pit | EOL as per schedule | Proactive Maintenance | EOL Replacement | N | Y | Y | OEM |  | Day | No | NA | Yes | Yes
126 | Fire and Safety | EOL as per schedule | Proactive Maintenance | EOL Replacement | Y | Y | Y | OEM |  | Day | Yes | To be discussed | Yes | Yes
127 | FM-200 | EOL as per schedule | Proactive Maintenance | EOL Replacement | Y | Y | Y | OEM |  | Day | Yes | To be discussed | Yes | Yes
128 | HT Panel | EOL as per schedule | Proactive Maintenance | EOL Replacement | Y | Y | Y | OEM |  | Day | Yes | To be discussed | Yes | Yes
129 | Inverter | EOL as per schedule | Proactive Maintenance | EOL Replacement | N | Y | Y | OEM |  | Night | No | NA | Yes | Yes
130 | Isolation Transformer | EOL as per schedule | Proactive Maintenance | EOL Replacement | Y | Y | Y | OEM |  | Night | No | NA | Yes | Yes
131 | LT Panel | EOL as per schedule | Proactive Maintenance | EOL Replacement | Y | Y | Y | OEM |  | Day | Yes | To be discussed | Yes | Yes
132 | PAS | EOL as per schedule | Proactive Maintenance | EOL Replacement | N | Y | Y | OEM |  | Day | No | NA | Yes | Yes
133 | PFE | EOL as per schedule | Proactive Maintenance | EOL Replacement | N | Y | Y | O&M |  | Day | No | NA | Yes | Yes
134 | RRS | EOL as per schedule | Proactive Maintenance | EOL Replacement | N | Y | Y | OEM |  | Day | No | NA | Yes | Yes
135 | Servo Stabilizer | EOL as per schedule | Proactive Maintenance | EOL Replacement | N | Y | Y | OEM |  | Day | No | NA | Yes | Yes
136 | Smoke Detector | EOL as per schedule | Proactive Maintenance | EOL Replacement | Y | Y | Y | OEM |  | Day | Yes | To be discussed | Yes | Yes
137 | SMPS- Vertiv | EOL as per schedule | Proactive Maintenance | EOL Replacement | Y | Y | Y | OEM |  | Night | Yes | To be discussed | Yes | Yes
138 | SMPS- Delta | EOL as per schedule | Proactive Maintenance | EOL Replacement | Y | Y | Y | OEM |  | Night | Yes | To be discussed | Yes | Yes
139 | SMPS BB | EOL as per schedule | Proactive Maintenance | EOL Replacement | Y | Y | Y | OEM |  | Night | No | NA | Yes | Yes
140 | Solar System | Monthly | Not Required as no activity involved | Monthly Reading | N | N | N | O&M |  | Day | No | NA | Yes | Yes
141 | Solar System | EOL as per schedule | Proactive Maintenance | EOL Replacement | N | Y | Y | OEM |  | Day | No | NA | Yes | Yes
142 | Transformer | EOL as per schedule | Proactive Maintenance | EOL Replacement | Y | Y | Y | OEM |  | Day | Yes | To be discussed | Yes | Yes
143 | UPS | EOL as per schedule | Proactive Maintenance | EOL Replacement | Y | Y | Y | OEM |  | Night | Yes | To be discussed | Yes | Yes
144 | UPS BB | EOL as per schedule | Proactive Maintenance | EOL Replacement | Y | Y | Y | OEM |  | Night | No | NA | Yes | Yes
145 | VESDA | EOL as per schedule | Proactive Maintenance | EOL Replacement | Y | Y | Y | OEM |  | Day | Yes | To be discussed | Yes | Yes
146 | WLD | EOL as per schedule | Proactive Maintenance | EOL Replacement | Y | Y | Y | OEM |  | Day | Yes | To be discussed | Yes | Yes
147 | All Active Racks | Yearly | Proactive Maintenance | DR Test | Y | Y | Y | O&M |  | Night | No | NA | Yes | Yes

## Sheet2
Where alarms generated at NOC | CRQ required
Day time activity | Where only alarms will be generated and will last for e.g 10 mins, 15 mins
Challenges for PM activities | Honeywell - for 7 days
EOL will be under Proactive maintenance
Pre- Photo & Post photo | Where physically performing any activity